Battery Monitoring System

(Battery monitoring system for larger UPS systems)

METHOD OF STATEMENT FOR

INSTALLATION AND COMMISSIONING

Table of content

1	BTMS Installation	4

1.1	Base System	4

1.1.1	Install BM-CS	4

1.1.2	Install BM-HS	5

1.1.3	Install BM-SS	5

1.1.4	Install BM-GW	5

1.1.5	Install BM-PS	6

1.1.6	Install BM-MC	6

1.1.7	Install BM-HMI	6

1.1.8	Install BM-TH	7

1.2	Power ON	7

2	BTMS commissioning	8

2.1	General settings	8

2.1.1	Network settings	8

2.1.2	NTP settings	9

2.1.3	Time settings	9

2.1.4	Users Setting	10

2.1.5	SMTP settings	10

2.1.6	SMS notifications	11

2.1.7	Modbus server	11

2.1.8	Project settings	11

2.2	Adding string and battery sensors	12

2.2.1	Assign string sensor to string	13

2.2.2	Assign string to UPS	14

2.2.3	Adding BM-MC, BM-LC and BM-TH	14

2.2.4	Validate Configuration	16

2.2.5	Check Settings	17

2.3	String and Battery sensors settings	18

2.3.1	Alarm settings	18

2.3.2	Resistance settings	20

2.3.3	Balancing settings	20

2.3.4	Cell settings	21

2.3.5	Hall Setting	21

2.3.6	Voltage Measurement	22

2.3.7	Conﬁguration ﬁle	23

3	Troubleshooting	25

BTMS Installation

Following steps to be done before start installation:

Disconnect the UPS from batteries by switch off battery breaker

Break string to small segments where total voltage doesn’t reach 50 V

Provide a place to install BTMS panel which includes below

BM-PS in (Power supply)

BM-GW (Gateway)

BTMS LAN switch (Network switch)

BM-MC (Master controller)

BM-HMI (and communication adapter CAD-232-A2-IQ)

Provide space to install below component on the battery cabinet

BM-SS (String sensor)

BM-CS (Cell sensor)

BM-HS (Hall sensor)

Base System

Install BM-CS

Connect red / black wires to battery terminals (Use original cables as they are)

Mount on battery with supplied 3M double sided stickers

Plug in red / black battery cable connector in

Connect the sensors with included white RJ9-RJ9 cables

1st OUT port (right) to 2nd IN port (left),

2nd OUT port (right) to 3rd IN port (left),

Max 60 BM-CS in one line

Install BM-HS

Unscrew split core and put around + wire from UPS to string

Arrow is pointing from UPS to 1st battery

Install BM-SS

Mount on DIN rail near the 1st string battery

Connect BM-HS with included 4-pin flat cable

Connect 1st battery BM-CS with included white RJ9-RJ9 cable

Connect 1st battery BM-CS of second line (if needed)

Power supply (+24 Vdc) from battery monitoring panel

Install BM-GW

Mount in distribution cabinet on DIN rail with the included bracket

Install BTMS LAN switch

Mount in distribution cabinet or LAN cabinet

Plug the power supply into the appropriate socket

Connect LAN cables to BM-GW

Pull the LAN cables to the BM-SS but do not connect them to the LAN switch (Properly mark which cable goes to which BM-SS)

Install BM-PS

Check that the BM-PS capacity (3.8 A) is sufficient for all devices powered by the PS power supply

If the consumption exceeds the capacity of the power supply divide the consumers into groups and uses several power supplies

Make sure that circuit breaker is switched OFF

Mount BM-PC on DIN rail in distribution cabinet

Connect AC L & N terminals

Connect DC + & - terminals to

  - All BM-SS

  - BM-GW

Install BM-MC

Mount in distribution cabinet on DIN rail

Connect DC power supply +24 V & GND terminals to + & - of power supply terminals

Connect LAN cable to BTMS LAN switch

Install BM-HMI

Mount CAD-232-A2-IQ adapter on DIN rail next to BM-MC

Ensure that the connecting cable (short RJ9 to RJ9) to the BM-MC is correctly inserted

Connect BM-MC COM 2 port with CAD-232-A2-IQ adapter bottom port (it doesn't matter which one)

Connect BM-HMI A & B terminals to CAD-232-A2-IQ A & B terminals

Connect BM-HMI +24 V & GND terminals to + & - BM-PS terminals

Install BM-TH

Mount BM-TH on wall next to string

Pull communication bus and power supply to BM-MC - do not connect to BM-TH

Communication bus must follow rules for RS-485 wiring

  - Bus line (no branching)

  - Use twisted pair shielded cable

  - Shield connected ONLY to one end of line

  - Terminate line with 120-ohm resistor on both side

  - Max length 1200 m

Power ON

Visually inspect wiring

Power on BM-PS circuit breaker

Check that all devices that are powered by the power adapter are turned on and are working stably (the LED indicators are lit continuously)

BTMS commissioning

Connect the laptop to the BTMS LAN switch

Set the IP on the laptop to 192.168.10.20

Open the address 192.168.10.1 in the Internet browser

Login with default username (admin) and default password (bmgw!admin)

General settings

Network settings

Select Settings - General tab

Set the parameters for the WAN interface

NTP settings

if necessary / requested set the parameters for an additional NTP (Network Time Protocol) server

Time settings

Set the desired time zone

Users Setting

Change (and remember!) the admin password

Add users

SMTP settings

Set the parameters for the SMTP (e-mail) server

SMS notifications

Test SMS messaging

Modbus server

Edit Modbus settings

Project settings

Set project information

The project name is displayed as root in the tree menu

You can also change the logo that appears above the tree menu

Adding string and battery sensors

Select Settings - Configuration tab

Connect a string sensor (always only one new-one at a time)

In the New unassigned BM-SS table (below main table) OK should appear for COM Status and HALL

To set the battery sensors press the Configure cells button

In Cell sensor addressing dialog box

Press Auto-sensing

Wait that Address searching status change to 3

Check whether all battery sensors have been found

If all sensors found then confirm with the Check & Write button

If the number of sensors found does not match the expected check sensor

Cabling and repeat Auto-sensing

Assign string sensor to string

Press Assign BM-SS

In Assign BM-SS dialog box select to which string BM-SS should be assigned

Assign string to UPS

In main table select row

Press Edit UPS

In Edit UPS dialog

  - Select UPS ID

  - Set name for UPS

Subsequent movement or reassignment of BM-SS sensors to another string and automatic reconfiguration of battery sensors is also possible

Repeat the process for all string sensors

Adding BM-MC, BM-LC and BM-TH

Select Settings - Configuration tab

Select BM-MC controller in main table 1st row right side

Press BM-LC Auto-address to discover connected BM-LC IO modules

If the modules are connected correctly, the statuses in the right 3 columns should change

Connect BM-TH temperature and humidity sensor (only one new sensor at a time)

The data of the connected sensor should appear in the New unassigned BM-TH table below the main table

Use the Assign BM-TH button to determine which string the sensor belongs to

Repeat for all BM-TH sensors

Validate Configuration

Check whether the data in the main table reflect the actual desired state

Confirm the configuration with the Apply configuration button above the table

The tree menu on the left side should refresh and reflect the actual status of the UPS and strings connected to the BM-GW

Check Settings

Switch the laptop to the facility network

Set the IP on the laptop according to the requirements for the facility LAN

Use the Internet browser to go to the address you set for the WAN connection

String and Battery sensors settings

To set up an individual BTMS string sensor, just select it in the tree structure on the left and select the Settings view.

Alarm settings

The conditions for triggering and automatic alarm reset are set for the string and for all batteries within the string.

Editing of the settings is enabled with the Edit button above the table.

Limit values are set in the left part of the table, and the action that the alarm triggers is set in the right part. The action can be sending an SMS or/and e-mail message or/and triggering a digital output.

Use the Write button to use the entered changes. The “Cancel” button cancels all changes.

The Recommend button presets some alarm parameters depending on the connected batteries and the used Hall sensor.

The proposed values can then be further adapted to the requirements and entered.

Resistance settings

Here we set the battery resistance measurement frequency.

Balancing settings

Battery balancing can be enabled or disabled. If balancing is enabled, set the threshold value at which balancing is triggered and the balancing execution interval.

Cell settings

For the proper functioning of battery status monitoring, it is necessary to specify what batteries are used in the string.

Hall Setting

Select the sensor used from the values offered.

The Zero calibration button is used to calibrate the Hall sensors.

It is important to ensure that during calibration the string current is 0 A

Voltage Measurement

The string sensor allows 2 ways of measuring the string voltage: as the sum of the voltage of the batteries in the string or directly. Since we have to work with dangerously high voltage when measuring the voltage directly, it is recommended to use the summation of the voltage of individual batteries where possible.

Conﬁguration ﬁle

It is possible to easily save the string sensor settings to a ﬁle.

And reading all the instructions from this one.

If we drag and drop the saved ﬁle onto the settings table, only the parameters that are in the table will be entered from the ﬁle.

Troubleshooting

If you are having problems with the system, try the appropriate solutions below. This may fix a system error that is the result of one of the most common system failures or installation mistakes. In any case, our technical support will be able to help you, it is at in http://support.robotina.com.

By trying the solutions listed below, our technical support will also be more effective in identifying errors and will help you more effectively.

The power supply and the power supply of all components are connected correctly

Communication cables are properly connected (it is best to check each one step by step)

Check that the hall sensor is facing correctly (there is an arrow on it showing the direction of the electric current)

Check LED on Cell sensor and String master (is green breathing mode or constant red)

One of the possible causes of malfunction may also be incorrect initial system configuration.

The initial configuration of the system can only be done by an authorized person! Contact an authorized person for any problems.

Robotina Help Desk in http://support.robotina.com